## All data
| A12 W35 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-07-04 | Techneco | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 30.1128 | 35.0987 | 1.4929 | no | 9.8955 | 8628.7753 | 2022.2983 | 4.2796 | yes | no | no | no | Test 0233 - Current release | 10
| 2019-07-04 | Techneco | GP561 | B26Hx26 | R32 | 980 | 240 | 98.4 | 30.139 | 35.1709 | 1.4725 | no | 9.9798 | 8589.4443 | 2044.1492 | 4.2146 | yes | no | no | no | Test 0234 - Current release | 10
| 2019-07-04 | Techneco | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 30.0812 | 35.0297 | 1.3321 | no | 8.4879 | 7641.7973 | 1748.7238 | 4.3831 | yes | no | no | no | Test 0235 | 10
| 2019-07-05 | Techneco | GP561 | B26Hx26 | R32 | 980 | 200 | 78 | 30.2097 | 35.1185 | 1.2079 | no | 7.2433 | 6873.7837 | 1477.2597 | 4.6671 | yes | no | no | no | Test 0236 | 10
| 2019-07-05 | Techneco | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 30.0961 | 35.0504 | 1.0508 | no | 6.1006 | 6035.4402 | 1248.4972 | 4.8487 | yes | no | no | no | Test 0237 | 10
| 2019-07-05 | Techneco | GP561 | B26Hx26 | R32 | 980 | 160 | 58.2 | 30.1272 | 35.056 | 0.97619 | no | 5.8944 | 5577.8223 | 1050.5967 | 5.3251 | yes | no | no | no | Test 0238 | 10
| 2019-07-05 | Techneco | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 30.1258 | 35.1248 | 0.79358 | no | 4.6777 | 4599.0189 | 834.9834 | 5.5246 | yes | no | no | no | Test 0239 | 10
| 2019-07-15 | Techneco | GP561 | B26Hx26 | R32 | 980 | 120 | 42 | 30.0702 | 35.124 | 0.62956 | no | 3.548 | 3688.431 | 632.2928 | 5.8509 | yes | no | no | no | Test 0240 | 10
| 2019-07-15 | Techneco | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 30.0828 | 35.151 | 0.45911 | no | 2.6483 | 2697.5201 | 467.2762 | 5.7903 | yes | no | no | no | Test 0242 | 10
| A12 W45 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-07-17 | Techneco | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 40.0721 | 45.13 | 1.2197 | no | 9.8627 | 6045.5003 | 2034.2418 | 3.5263 | yes | no | no | no | Test 0244 - Current release | 10
| 2019-07-17 | Techneco | GP561 | B26Hx26 | R32 | 980 | 240 | 98.4 | 40.0941 | 45.1349 | 1.2163 | no | 9.8683 | 7107.439 | 2038.0663 | 3.4979 | yes | no | no | no | Test 0245 - Current release | 10
| 2019-07-17 | Techneco | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 40.0885 | 45.0549 | 1.2276 | no | 9.8849 | 7067.6887 | 2021.3591 | 3.507 | yes | no | no | no | Test 0246 - Current release | 10
| 2019-07-17 | Techneco | GP561 | B26Hx26 | R32 | 980 | 200 | 78 | 40.0682 | 45.0471 | 1.1606 | no | 8.882 | 6699.1561 | 1829.7901 | 3.6722 | yes | no | no | no | Test 0247 | 10
| 2019-07-19 | Techneco | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 40.1126 | 45.0573 | 1.0064 | no | 7.4883 | 5769.3496 | 1543.0276 | 3.7502 | yes | no | no | no | Test 0248 | 10
| 2019-07-19 | Techneco | GP561 | B26Hx26 | R32 | 980 | 160 | 58.2 | 40.0896 | 45.1048 | 0.91793 | no | 6.2896 | 5336.9388 | 1301.1768 | 4.1139 | yes | no | no | no | Test 0249 | 10
| 2019-07-19 | Techneco | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 40.0435 | 44.9626 | 0.73991 | no | 5.9349 | 4219.4372 | 1060.1436 | 3.9921 | yes | no | no | no | Test 0250 | 10
| 2019-07-19 | Techneco | GP561 | B26Hx26 | R32 | 980 | 120 | 42 | 40.0775 | 44.9263 | 0.58534 | no | 4.5499 | 3290.2776 | 815.0166 | 4.0493 | yes | no | no | no | Test 0251 | 10
| 2019-07-22 | Techneco | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 39.924 | 43.3408 | 0.59043 | no | 3.3461 | 2338.7102 | 589.7238 | 3.9777 | yes | no | no | no | Test 0252 | 10
| A12 W55 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 240 | 98.4 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 200 | 78 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 160 | 58.2 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 140 | 48 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 120 | 42 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
|  | Techneco | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 |  |  |  | no |  |  |  |  | yes | no | no | no |  | 10
__ | __________ | ____________ | _______ | ________ | ___________ | _______ | _________ | _________ | _________ | _________ | ______ |  |  | __________ | _________ | ______ | ____________ | _________ | _______ | _____________ | _____________________________________________
| A7 W35 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-18 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 29.7509 | 34.975 | 1.1564 | yes | 10.979 | 7003.1753 | 2094.7641 | 3.3432 | yes | no | no | no | Defrost cycle included | 10
| 2019-04-18 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 250 | 103.2 | 30.4303 | 35.6007 | 1.1562 | yes | 10.894 | 6930.1051 | 2066.4618 | 3.3536 | yes | no | no | no | Defrost cycle included | 10
| 2019-04-18 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 240 | 98.4 | 30.5493 | 35.54 | 1.157 | yes | 9.926 | 6694.2171 | 1953.2961 | 3.4271 | yes | no | no | no | Defrost cycle included | 10
| 2019-05-03 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 230 | 93 | 29.8666 | 34.6349 | 1.1628 | yes | 9.255 | 6427.9028 | 1769.7431 | 3.6321 | yes | no | no | no | Defrost cycle included | 10
| 2019-05-04 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 29.7805 | 35.081 | 1.1625 | yes | 8.568 | 7143.7217 | 1734.4666 | 4.1187 | yes | no | no | no | Defrost cycle > 3 hours | 10
| 2019-05-04 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 210 | 86.4 | 29.7349 | 34.5325 | 1.1619 | no | 8.411 | 6462.1145 | 1508.1757 | 4.2847 | yes | no | no | no |  | 10
| 2019-05-05 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 200 | 78 | 29.7576 | 34.434 | 1.1618 | no | 7.115 | 6298.4762 | 1433.1706 | 4.3948 | yes | no | no | no |  | 10
| 2019-04-20 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 30.4659 | 34.6569 | 1.1581 | no | 5.988 | 5626.8987 | 1260.8976 | 4.4626 | yes | no | no | no |  | 10
| 2019-05-06 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 29.7427 | 33.8704 | 1.1613 | no | 6.426 | 5556.9219 | 1202.3305 | 4.6218 | yes | no | no | no |  | 10
| 2019-04-20 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 160 | 58.2 | 30.4464 | 34.1999 | 1.1578 | no | 5.844 | 5038.1029 | 1046.0134 | 4.8165 | yes | no | no | no |  | 10
| 2019-04-20 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 30.4595 | 33.5383 | 1.1578 | no | 4.603 | 4132.5819 | 823.5499 | 5.018 | yes | no | no | no |  | 10
| 2019-04-20 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 120 | 42 | 30.4868 | 33.2152 | 1.1574 | no | 3.928 | 3660.7586 | 706.1911 | 5.1838 | yes | no | no | no |  | 10
| 2019-04-20 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 30.5336 | 32.4193 | 1.1568 | no | 2.587 | 2528.7339 | 461.1996 | 5.4829 | yes | no | no | no |  | 10
| A7 W45 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-20 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 39.6959 | 45.0154 | 1.0852 | yes | 12.391 | 6692.48 | 2494.4246 | 2.683 | yes | no | no | no | Defrost cycle included | 10
| 2019-04-21 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 250 | 103.2 | 39.7145 | 45.232 | 1.0849 | yes | 12.334 | 6939.3334 | 2500.7026 | 2.775 | yes | no | no | no | Defrost cycle > 3 hours | 10
| 2019-04-21 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 240 | 98.4 | 39.6888 | 44.89 | 1.085 | yes | 11.929 | 6542.1924 | 2394.368 | 2.7323 | yes | no | no | no | Defrost cycle > 3 hours | 10
| 2019-04-21 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 230 | 93 | 39.721 | 45.3979 | 1.0844 | no | 11.134 | 7136.8048 | 2350.8678 | 3.0358 | yes | no | no | no |  | 10
| 2019-04-21 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 39.645 | 44.9415 | 1.0948 | no | 10.178 | 6722.4482 | 2149.2013 | 3.1279 | yes | no | no | no |  | 10
| 2019-04-22 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 210 | 86.4 | 39.7455 | 44.9516 | 1.0953 | no | 10.011 | 6610.7237 | 2102.8202 | 3.1437 | yes | no | no | no |  | 10
| 2019-04-22 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 200 | 78 | 39.6828 | 44.4096 | 1.0953 | no | 8.642 | 6001.9396 | 1816.7682 | 3.3036 | yes | no | no | no |  | 10
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 39.7897 | 43.6765 | 1.0953 | no | 7.234 | 4935.171 | 1524.3451 | 3.2376 | yes | no | no | no |  | 10
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 160 | 58.2 | 39.6074 | 43.0768 | 1.0951 | no | 5.981 | 4404.4839 | 1264.1502 | 3.4841 | yes | no | no | no |  | 10
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 39.6531 | 42.3916 | 1.0945 | no | 5.654 | 3474.675 | 979.8285 | 3.5462 | yes | no | no | no |  | 10
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 120 | 42 | 39.8158 | 42.2754 | 1.0952 | no | 4.926 | 3122.8471 | 883.6212 | 3.5341 | yes | no | no | no |  | 10
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 39.756 | 41.2013 | 1.0953 | no | 3.218 | 1835.2918 | 575.4679 | 3.1892 | yes | no | no | no |  | 10
| A7 W55 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-05-02 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 49.3668 | 54.3664 | 1.0013 | no | 12.38 | 5803.6858 | 2558.6461 | 2.2683 | yes | no | no | no | Unstable conditions, results are arbitrary | 10
| 2019-05-02 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 250 | 103.2 | 49.6627 | 54.1793 | 1.0555 | no | 12.126 | 5526.4081 | 2416.7833 | 2.2867 | yes | no | no | no | Unstable conditions, results are arbitrary | 10
| 2019-05-03 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 240 | 98.4 | 49.649 | 54.1683 | 1.0556 | no | 12.321 | 5530.4565 | 2405.2069 | 2.2994 | yes | no | no | no | Unstable conditions, results are arbitrary | 10
| 2019-05-03 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 49.4504 | 53.0361 | 1.0555 | no | 8.702 | 4387.6718 | 1713.6534 | 2.5604 | yes | no | no | no | Unstable conditions, results are arbitrary | 10
| A2 W35 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-16 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 29.2618 | 34.3325 | 1.1575 | yes | 10.931 | 6804.1734 | 2157.9949 | 3.153 | yes | no | no | no |  | 11.6667
| 2019-04-17 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 28.9635 | 33.6696 | 1.1566 | yes | 8.441 | 6310.0376 | 1753.9105 | 3.5977 | yes | no | no | no | Defrost cycle > 3 hours | 11.6667
| 2019-04-17 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 31.3334 | 34.5005 | 1.1559 | yes | 6.974 | 4243.8366 | 1252.1499 | 3.3892 | yes | no | no | no | Defrost cycle > 3 hours | 11.6667
| 2019-04-17 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 32.0701 | 34.665 | 1.1554 | ? | 4.983 | 3475.5644 | 892.6959 | 3.8933 | yes | no | no | no | Unsure if defrost would occur | 11.6667
| 2019-04-17 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 33.3875 | 34.6744 | 1.1543 | ? | 2.921 | 1722.0681 | 499.3726 | 3.4485 | yes | no | no | no | Unsure if defrost would occur | 10
| A2 W45 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-17 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 40.3872 | 45.2127 | 1.083 | yes | 12.395 | 6058.7964 | 2511.6478 | 2.4123 | yes | no | no | no | Defrost cycle > 3 hours | 11.6667
| 2019-04-17 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 40.204 | 44.3073 | 1.0929 | yes | 10.168 | 5198.6167 | 2031.8338 | 2.5586 | yes | no | no | no | Defrost cycle > 3 hours | 11.6667
| 2019-04-18 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 40.2287 | 43.4444 | 1.0923 | yes | 7.282 | 4071.8312 | 1516.4586 | 2.6851 | yes | no | no | no | Defrost cycle > 3 hours | 11.6667
| 2019-04-18 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 40.467 | 42.9388 | 1.0933 | no | 6.053 | 3132.9614 | 1063.8925 | 2.9448 | yes | no | no | no |  | 11.6667
| 2019-04-18 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 43.5058 | 44.6452 | 1.0932 | no | 3.57 | 1443.9843 | 633.0049 | 2.2812 | yes | no | no | no |  | 10
| A2 W55 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 48.6932 | 54.3024 | 0.68327 | yes | 12.232 | 4443.0697 | 2414.3846 | 1.8402 | yes | no | no | no | Flow lower than requested (1,06) & no full defrost cycle | 11.6667
| 2019-04-23 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 48.5409 | 53.9797 | 0.68092 | yes | 11.675 | 4293.3593 | 2294.2294 | 1.8714 | yes | no | no | no | Flow lower than requested (1,06) & Defrost cycle > 3 hours | 11.6667
| 2019-04-24 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 48.6104 | 53.5211 | 0.68139 | yes | 8.774 | 3879.1158 | 1835.9497 | 2.1129 | yes | no | no | no | Flow lower than requested (1,06) | 11.6667
| 2019-04-24 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 48.6163 | 52.2043 | 0.68 | no | 6.236 | 2828.4204 | 1260.9779 | 2.243 | yes | no | no | no | Flow lower than requested (1,06) | 11.6667
| 2019-04-24 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 48.6497 | 50.3293 | 0.68063 | no | 4.232 | 1325.3079 | 752.9151 | 1.7602 | yes | no | no | no | Flow lower than requested (1,06) | 10
| A-7 W35 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-24 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 30.5762 | 34.2502 | 1.1557 | yes | 10.259 | 4922.2233 | 1958.9899 | 2.5126 | yes | no | no | no | Averaged over 1 full cycle, but there would be 2 in 3 hours | 11.6667
| 2019-04-24 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 30.6649 | 33.8739 | 1.1553 | yes | 8.101 | 4297.8099 | 1599.147 | 2.6876 | yes | no | no | no |  | 11.6667
| 2019-04-24 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 30.5143 | 32.9842 | 1.1552 | yes | 6.706 | 3307.7116 | 1187.6682 | 2.785 | yes | no | no | no |  | 11.6667
| 2019-04-25 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 30.6035 | 32.4422 | 1.1555 | yes | 7.13 | 2462.9423 | 822.4511 | 2.9946 | yes | no | no | no | no full defrost cycle measured | 11.6667
| 2019-04-25 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 30.597 | 31.6023 | 1.1551 | yes | 6.848 | 1346.2666 | 531.3308 | 2.5338 | yes | no | no | no |  | 11.6667
| A-7 W45 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-25 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 40.9822 | 44.6671 | 1.1042 | yes | 12.174 | 4716.8698 | 2380.2043 | 1.9817 | yes | no | no | no |  | 11.6667
| 2019-04-25 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 40.6645 | 43.7859 | 1.093 | yes | 9.606 | 3955.1349 | 1911.4088 | 2.0692 | yes | no | no | no |  | 11.6667
| 2019-04-26 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 40.753 | 43.2114 | 1.0931 | yes | 7.203 | 3115.2881 | 1436.1389 | 2.1692 | yes | no | no | no |  | 11.6667
| 2019-04-26 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 40.77 | 42.4755 | 1.0927 | yes | 6.718 | 2160.3795 | 1009.1906 | 2.1407 | yes | no | no | no |  | 11.6667
| 2019-04-26 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 40.7244 | 41.4543 | 1.0928 | yes | 6.93 | 924.6794 | 633.0724 | 1.4606 | yes | no | no | no | no full defrost cycle measured | 11.6667
| A-7 W55 | [20 empty] | fan
| Date | Test location | ODU | P.H.E. | Refrigerant | Charge | Setpoint | Frequency | Water in | Water out | Flow | Defrosts | Current (max) | Power out | Power In | COP | Toshiba PCBs | Main PCB | Pump | Corrected COP | Remarks | rotation
| - | - | - | - | type | g | - | Hz | °C | °C | m³/h | yes/no | A | W | W | - | yes/no | yes/no | yes/no | yes/no | - | [Hz]
| 2019-04-30 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 254 | 105.6 | 49.6441 | 54.203 | 0.66589 | yes | 12.392 | 3519.2536 | 2367.0038 | 1.4868 | yes | no | no | no | Flow lower than requested (1,06) & unit shut off mid test | 11.6667
| 2019-05-01 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 220 | 88.2 | 49.6441 | 54.2416 | 0.66525 | yes | 11.693 | 3545.6444 | 2262.5517 | 1.5671 | yes | no | no | no | Flow lower than requested (1,06), many protect functions | 11.6667
| 2019-05-01 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 180 | 68.4 | 49.6102 | 53.1824 | 0.66575 | yes | 8.385 | 2757.0487 | 1684.5235 | 1.6367 | yes | no | no | no | Flow lower than requested (1,06), unstable conditions | 11.6667
| 2019-05-01 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 140 | 48 | 49.5824 | 51.689 | 0.66589 | yes | 7.298 | 1626.2074 | 1171.696 | 1.3879 | yes | no | no | no | Flow lower than requested (1,06), unstable conditions | 11.6667
| 2019-05-01 | Mertzwiller | GP561 | B26Hx26 | R32 | 980 | 100 | 28.8 | 48.8487 | 49.0278 | 0.6667 | yes | 6.489 | 138.3712 | 735.9922 | 0.18801 | yes | no | no | no | Weird behavior, unknown why (T_delta = 0,18 °C) | 11.6667

## DATA 1 NO DEFROST corrected
[10 empty] | DT | 10 | [s]
INPUT |  |  |  |  | OUTPUT |  |  |  |  | Start | 0 | [s] | [15 empty] | y_HP_Power | y_Power_All
[10 empty] | Compr_freq |  |  |  | Tair |  |  | Twater in |  |  | Qwater |  |  |  | Twater out
Time | Frequ | Tair | Twater in | Qwater | Time | y_Heat_Power | y_Elec_Power | Twater out | COP
[s] | [Hz] | [°C] | [°C] | [m3/s] | [s] | [W] | [W] | [°C] |  | Time | [Hz] |  | A12 W35 | Time | [°C] |  | Time | [°C] |  | Time | [m3/s] | [m3/s] | [m3/h] | Time | [m3/s] | [m3/s] | Time | Tair
0 | 88.2 | 12 | 30.0812 | 0.00037003 | 0 | 7641.7973 | 1748.7238 | 35.0297 | 4.3699 | 0 | 88.2 |  | 88.2 | 0 | 12 | 12 | 0 | 30.0812 | 30.0812 | 0 | 0.00037003 | 0.00037003 | 1.3321 | 0 | 35.0297 | 35.0297 | 0 | 7641.7973 | 1748.7238 | 7641.7973 | 1748.7238
10 | 88.2 | 12 | 30.0812 | 0.00037003 | 10 | 7641.7973 | 1748.7238 | 35.0297 | 4.3699 | 10 | 88.2 |  | 78 | 10 | 12 | 12 | 10 | 30.0812 | 30.2097 | 10 | 0.00037003 | 0.00033553 | 1.2079 | 10 | 35.0297 | 35.1185 | 10 | 7641.7973 | 1748.7238 | 6873.7837 | 1477.2597
10 | 78 | 12 | 30.2097 | 0.00033553 | 10 | 6873.7837 | 1477.2597 | 35.1185 | 4.6531 | 10 | 78 |  | 68.4 | 10 | 12 | 12 | 10 | 30.2097 | 30.0961 | 10 | 0.00033553 | 0.0002919 | 1.0508 | 10 | 35.1185 | 35.0504 | 10 | 6873.7837 | 1477.2597 | 6035.4402 | 1248.4972
20 | 78 | 12 | 30.2097 | 0.00033553 | 20 | 6873.7837 | 1477.2597 | 35.1185 | 4.6531 | 20 | 78 |  | 58.2 | 20 | 12 | 12 | 20 | 30.2097 | 30.1272 | 20 | 0.00033553 | 0.00027116 | 0.97619 | 20 | 35.1185 | 35.056 | 20 | 6873.7837 | 1477.2597 | 5577.8223 | 1050.5967
20 | 68.4 | 12 | 30.0961 | 0.0002919 | 20 | 6035.4402 | 1248.4972 | 35.0504 | 4.8342 | 20 | 68.4 |  | 48 | 20 | 12 | 12 | 20 | 30.0961 | 30.1258 | 20 | 0.0002919 | 0.00022044 | 0.79358 | 20 | 35.0504 | 35.1248 | 20 | 6035.4402 | 1248.4972 | 4599.0189 | 834.9834
30 | 68.4 | 12 | 30.0961 | 0.0002919 | 30 | 6035.4402 | 1248.4972 | 35.0504 | 4.8342 | 30 | 68.4 |  | 42 | 30 | 12 | 12 | 30 | 30.0961 | 30.0702 | 30 | 0.0002919 | 0.00017488 | 0.62956 | 30 | 35.0504 | 35.124 | 30 | 6035.4402 | 1248.4972 | 3688.431 | 632.2928
30 | 58.2 | 12 | 30.1272 | 0.00027116 | 30 | 5577.8223 | 1050.5967 | 35.056 | 5.3092 | 30 | 58.2 |  | 28.8 | 30 | 12 | 12 | 30 | 30.1272 | 30.0828 | 30 | 0.00027116 | 0.00012753 | 0.45911 | 30 | 35.056 | 35.151 | 30 | 5577.8223 | 1050.5967 | 2697.5201 | 467.2762
40 | 58.2 | 12 | 30.1272 | 0.00027116 | 40 | 5577.8223 | 1050.5967 | 35.056 | 5.3092 | 40 | 58.2 |  |  | 40 | 12 |  | 40 | 30.1272 |  | 40 | 0.00027116 |  |  | 40 | 35.056 |  | 40 | 5577.8223 | 1050.5967
40 | 48 | 12 | 30.1258 | 0.00022044 | 40 | 4599.0189 | 834.9834 | 35.1248 | 5.5079 | 40 | 48 |  |  | 40 | 12 |  | 40 | 30.1258 |  | 40 | 0.00022044 |  |  | 40 | 35.1248 |  | 40 | 4599.0189 | 834.9834
50 | 48 | 12 | 30.1258 | 0.00022044 | 50 | 4599.0189 | 834.9834 | 35.1248 | 5.5079 | 50 | 48 |  |  | 50 | 12 |  | 50 | 30.1258 |  | 50 | 0.00022044 |  |  | 50 | 35.1248 |  | 50 | 4599.0189 | 834.9834
50 | 42 | 12 | 30.0702 | 0.00017488 | 50 | 3688.431 | 632.2928 | 35.124 | 5.8334 | 50 | 42 |  |  | 50 | 12 |  | 50 | 30.0702 |  | 50 | 0.00017488 |  |  | 50 | 35.124 |  | 50 | 3688.431 | 632.2928
60 | 42 | 12 | 30.0702 | 0.00017488 | 60 | 3688.431 | 632.2928 | 35.124 | 5.8334 | 60 | 42 |  |  | 60 | 12 |  | 60 | 30.0702 |  | 60 | 0.00017488 |  |  | 60 | 35.124 |  | 60 | 3688.431 | 632.2928
60 | 28.8 | 12 | 30.0828 | 0.00012753 | 60 | 2697.5201 | 467.2762 | 35.151 | 5.7729 | 60 | 28.8 |  |  | 60 | 12 |  | 60 | 30.0828 |  | 60 | 0.00012753 |  |  | 60 | 35.151 |  | 60 | 2697.5201 | 467.2762
70 | 28.8 | 12 | 30.0828 | 0.00012753 | 70 | 2697.5201 | 467.2762 | 35.151 | 5.7729 | 70 | 28.8 |  | A12 W45 | 70 | 12 |  | 70 | 30.0828 |  | 70 | 0.00012753 |  |  | 70 | 35.151 |  | 70 | 2697.5201 | 467.2762
70 | 78 | 12 | 40.0682 | 0.0003224 | 70 | 6699.1561 | 1829.7901 | 45.0471 | 3.6612 | 70 | 78 |  | 78 | 70 | 12 | 12 | 70 | 40.0682 | 40.0682 | 70 | 0.0003224 | 0.0003224 | 1.1606 | 70 | 45.0471 | 45.0471 | 70 | 6699.1561 | 1829.7901 | 6699.1561 | 1829.7901
80 | 78 | 12 | 40.0682 | 0.0003224 | 80 | 6699.1561 | 1829.7901 | 45.0471 | 3.6612 | 80 | 78 |  | 68.4 | 80 | 12 | 12 | 80 | 40.0682 | 40.1126 | 80 | 0.0003224 | 0.00027957 | 1.0064 | 80 | 45.0471 | 45.0573 | 80 | 6699.1561 | 1829.7901 | 5769.3496 | 1543.0276
80 | 68.4 | 12 | 40.1126 | 0.00027957 | 80 | 5769.3496 | 1543.0276 | 45.0573 | 3.739 | 80 | 68.4 |  | 58.2 | 80 | 12 | 12 | 80 | 40.1126 | 40.0896 | 80 | 0.00027957 | 0.00025498 | 0.91793 | 80 | 45.0573 | 45.1048 | 80 | 5769.3496 | 1543.0276 | 5336.9388 | 1301.1768
90 | 68.4 | 12 | 40.1126 | 0.00027957 | 90 | 5769.3496 | 1543.0276 | 45.0573 | 3.739 | 90 | 68.4 |  | 48 | 90 | 12 | 12 | 90 | 40.1126 | 40.0435 | 90 | 0.00027957 | 0.00020553 | 0.73991 | 90 | 45.0573 | 44.9626 | 90 | 5769.3496 | 1543.0276 | 4219.4372 | 1060.1436
90 | 58.2 | 12 | 40.0896 | 0.00025498 | 90 | 5336.9388 | 1301.1768 | 45.1048 | 4.1016 | 90 | 58.2 |  | 42 | 90 | 12 | 12 | 90 | 40.0896 | 40.0775 | 90 | 0.00025498 | 0.0001626 | 0.58534 | 90 | 45.1048 | 44.9263 | 90 | 5336.9388 | 1301.1768 | 3290.2776 | 815.0166
100 | 58.2 | 12 | 40.0896 | 0.00025498 | 100 | 5336.9388 | 1301.1768 | 45.1048 | 4.1016 | 100 | 58.2 |  | 28.8 | 100 | 12 | 12 | 100 | 40.0896 | 39.924 | 100 | 0.00025498 | 0.00016401 | 0.59043 | 100 | 45.1048 | 43.3408 | 100 | 5336.9388 | 1301.1768 | 2338.7102 | 589.7238
100 | 48 | 12 | 40.0435 | 0.00020553 | 100 | 4219.4372 | 1060.1436 | 44.9626 | 3.9801 | 100 | 48 |  |  | 100 | 12 |  | 100 | 40.0435 |  | 100 | 0.00020553 |  |  | 100 | 44.9626 |  | 100 | 4219.4372 | 1060.1436
110 | 48 | 12 | 40.0435 | 0.00020553 | 110 | 4219.4372 | 1060.1436 | 44.9626 | 3.9801 | 110 | 48 |  |  | 110 | 12 |  | 110 | 40.0435 |  | 110 | 0.00020553 |  |  | 110 | 44.9626 |  | 110 | 4219.4372 | 1060.1436
110 | 42 | 12 | 40.0775 | 0.0001626 | 110 | 3290.2776 | 815.0166 | 44.9263 | 4.0371 | 110 | 42 |  |  | 110 | 12 |  | 110 | 40.0775 |  | 110 | 0.0001626 |  |  | 110 | 44.9263 |  | 110 | 3290.2776 | 815.0166
120 | 42 | 12 | 40.0775 | 0.0001626 | 120 | 3290.2776 | 815.0166 | 44.9263 | 4.0371 | 120 | 42 |  |  | 120 | 12 |  | 120 | 40.0775 |  | 120 | 0.0001626 |  |  | 120 | 44.9263 |  | 120 | 3290.2776 | 815.0166
120 | 28.8 | 12 | 39.924 | 0.00016401 | 120 | 2338.7102 | 589.7238 | 43.3408 | 3.9658 | 120 | 28.8 |  |  | 120 | 12 |  | 120 | 39.924 |  | 120 | 0.00016401 |  |  | 120 | 43.3408 |  | 120 | 2338.7102 | 589.7238
130 | 28.8 | 12 | 39.924 | 0.00016401 | 130 | 2338.7102 | 589.7238 | 43.3408 | 3.9658 | 130 | 28.8 |  | A7 W35 | 130 | 12 |  | 130 | 39.924 |  | 130 | 0.00016401 |  |  | 130 | 43.3408 |  | 130 | 2338.7102 | 589.7238
130 | 86.4 | 7 | 29.7349 | 0.00032274 | 130 | 6462.1145 | 1508.1757 | 34.5325 | 4.2847 | 130 | 86.4 |  | 86.4 | 130 | 7 | 7 | 130 | 29.7349 | 29.7349 | 130 | 0.00032274 | 0.00032274 | 1.1619 | 130 | 34.5325 | 34.5325 | 130 | 6462.1145 | 1508.1757 | 6462.1145 | 1508.1757
140 | 86.4 | 7 | 29.7349 | 0.00032274 | 140 | 6462.1145 | 1508.1757 | 34.5325 | 4.2847 | 140 | 86.4 |  | 78 | 140 | 7 | 7 | 140 | 29.7349 | 29.7576 | 140 | 0.00032274 | 0.00032273 | 1.1618 | 140 | 34.5325 | 34.434 | 140 | 6462.1145 | 1508.1757 | 6298.4762 | 1433.1706
140 | 78 | 7 | 29.7576 | 0.00032273 | 140 | 6298.4762 | 1433.1706 | 34.434 | 4.3948 | 140 | 78 |  | 68.4 | 140 | 7 | 7 | 140 | 29.7576 | 29.7427 | 140 | 0.00032273 | 0.00032257 | 1.1613 | 140 | 34.434 | 33.8704 | 140 | 6298.4762 | 1433.1706 | 5556.9219 | 1202.3305
150 | 78 | 7 | 29.7576 | 0.00032273 | 150 | 6298.4762 | 1433.1706 | 34.434 | 4.3948 | 150 | 78 |  | 58.2 | 150 | 7 | 7 | 150 | 29.7576 | 30.4464 | 150 | 0.00032273 | 0.00032161 | 1.1578 | 150 | 34.434 | 34.1999 | 150 | 6298.4762 | 1433.1706 | 5038.1029 | 1046.0134
150 | 68.4 | 7 | 29.7427 | 0.00032257 | 150 | 5556.9219 | 1202.3305 | 33.8704 | 4.6218 | 150 | 68.4 |  | 48 | 150 | 7 | 7 | 150 | 29.7427 | 30.4595 | 150 | 0.00032257 | 0.00032162 | 1.1578 | 150 | 33.8704 | 33.5383 | 150 | 5556.9219 | 1202.3305 | 4132.5819 | 823.5499
160 | 68.4 | 7 | 29.7427 | 0.00032257 | 160 | 5556.9219 | 1202.3305 | 33.8704 | 4.6218 | 160 | 68.4 |  | 42 | 160 | 7 | 7 | 160 | 29.7427 | 30.4868 | 160 | 0.00032257 | 0.00032149 | 1.1574 | 160 | 33.8704 | 33.2152 | 160 | 5556.9219 | 1202.3305 | 3660.7586 | 706.1911
160 | 58.2 | 7 | 30.4464 | 0.00032161 | 160 | 5038.1029 | 1046.0134 | 34.1999 | 4.8165 | 160 | 58.2 |  | 28.8 | 160 | 7 | 7 | 160 | 30.4464 | 30.5336 | 160 | 0.00032161 | 0.00032133 | 1.1568 | 160 | 34.1999 | 32.4193 | 160 | 5038.1029 | 1046.0134 | 2528.7339 | 461.1996
170 | 58.2 | 7 | 30.4464 | 0.00032161 | 170 | 5038.1029 | 1046.0134 | 34.1999 | 4.8165 | 170 | 58.2 |  |  | 170 | 7 |  | 170 | 30.4464 |  | 170 | 0.00032161 |  |  | 170 | 34.1999 |  | 170 | 5038.1029 | 1046.0134
170 | 48 | 7 | 30.4595 | 0.00032162 | 170 | 4132.5819 | 823.5499 | 33.5383 | 5.018 | 170 | 48 |  |  | 170 | 7 |  | 170 | 30.4595 |  | 170 | 0.00032162 |  |  | 170 | 33.5383 |  | 170 | 4132.5819 | 823.5499
180 | 48 | 7 | 30.4595 | 0.00032162 | 180 | 4132.5819 | 823.5499 | 33.5383 | 5.018 | 180 | 48 |  |  | 180 | 7 |  | 180 | 30.4595 |  | 180 | 0.00032162 |  |  | 180 | 33.5383 |  | 180 | 4132.5819 | 823.5499
180 | 42 | 7 | 30.4868 | 0.00032149 | 180 | 3660.7586 | 706.1911 | 33.2152 | 5.1838 | 180 | 42 |  |  | 180 | 7 |  | 180 | 30.4868 |  | 180 | 0.00032149 |  |  | 180 | 33.2152 |  | 180 | 3660.7586 | 706.1911
190 | 42 | 7 | 30.4868 | 0.00032149 | 190 | 3660.7586 | 706.1911 | 33.2152 | 5.1838 | 190 | 42 |  |  | 190 | 7 |  | 190 | 30.4868 |  | 190 | 0.00032149 |  |  | 190 | 33.2152 |  | 190 | 3660.7586 | 706.1911
190 | 28.8 | 7 | 30.5336 | 0.00032133 | 190 | 2528.7339 | 461.1996 | 32.4193 | 5.4829 | 190 | 28.8 |  |  | 190 | 7 |  | 190 | 30.5336 |  | 190 | 0.00032133 |  |  | 190 | 32.4193 |  | 190 | 2528.7339 | 461.1996
200 | 28.8 | 7 | 30.5336 | 0.00032133 | 200 | 2528.7339 | 461.1996 | 32.4193 | 5.4829 | 200 | 28.8 |  | A7 W45 | 200 | 7 |  | 200 | 30.5336 |  | 200 | 0.00032133 |  |  | 200 | 32.4193 |  | 200 | 2528.7339 | 461.1996
200 | 93 | 7 | 39.721 | 0.00030123 | 200 | 7136.8048 | 2350.8678 | 45.3979 | 3.0358 | 200 | 93 |  | 93 | 200 | 7 | 7 | 200 | 39.721 | 39.721 | 200 | 0.00030123 | 0.00030123 | 1.0844 | 200 | 45.3979 | 45.3979 | 200 | 7136.8048 | 2350.8678 | 7136.8048 | 2350.8678
210 | 93 | 7 | 39.721 | 0.00030123 | 210 | 7136.8048 | 2350.8678 | 45.3979 | 3.0358 | 210 | 93 |  | 88.2 | 210 | 7 | 7 | 210 | 39.721 | 39.645 | 210 | 0.00030123 | 0.00030412 | 1.0948 | 210 | 45.3979 | 44.9415 | 210 | 7136.8048 | 2350.8678 | 6722.4482 | 2149.2013
210 | 88.2 | 7 | 39.645 | 0.00030412 | 210 | 6722.4482 | 2149.2013 | 44.9415 | 3.1279 | 210 | 88.2 |  | 86.4 | 210 | 7 | 7 | 210 | 39.645 | 39.7455 | 210 | 0.00030412 | 0.00030426 | 1.0953 | 210 | 44.9415 | 44.9516 | 210 | 6722.4482 | 2149.2013 | 6610.7237 | 2102.8202
220 | 88.2 | 7 | 39.645 | 0.00030412 | 220 | 6722.4482 | 2149.2013 | 44.9415 | 3.1279 | 220 | 88.2 |  | 78 | 220 | 7 | 7 | 220 | 39.645 | 39.6828 | 220 | 0.00030412 | 0.00030425 | 1.0953 | 220 | 44.9415 | 44.4096 | 220 | 6722.4482 | 2149.2013 | 6001.9396 | 1816.7682
220 | 86.4 | 7 | 39.7455 | 0.00030426 | 220 | 6610.7237 | 2102.8202 | 44.9516 | 3.1437 | 220 | 86.4 |  | 68.4 | 220 | 7 | 7 | 220 | 39.7455 | 39.7897 | 220 | 0.00030426 | 0.00030424 | 1.0953 | 220 | 44.9516 | 43.6765 | 220 | 6610.7237 | 2102.8202 | 4935.171 | 1524.3451
230 | 86.4 | 7 | 39.7455 | 0.00030426 | 230 | 6610.7237 | 2102.8202 | 44.9516 | 3.1437 | 230 | 86.4 |  | 58.2 | 230 | 7 | 7 | 230 | 39.7455 | 39.6074 | 230 | 0.00030426 | 0.00030419 | 1.0951 | 230 | 44.9516 | 43.0768 | 230 | 6610.7237 | 2102.8202 | 4404.4839 | 1264.1502
230 | 78 | 7 | 39.6828 | 0.00030425 | 230 | 6001.9396 | 1816.7682 | 44.4096 | 3.3036 | 230 | 78 |  | 48 | 230 | 7 | 7 | 230 | 39.6828 | 39.6531 | 230 | 0.00030425 | 0.00030402 | 1.0945 | 230 | 44.4096 | 42.3916 | 230 | 6001.9396 | 1816.7682 | 3474.675 | 979.8285
240 | 78 | 7 | 39.6828 | 0.00030425 | 240 | 6001.9396 | 1816.7682 | 44.4096 | 3.3036 | 240 | 78 |  | 42 | 240 | 7 | 7 | 240 | 39.6828 | 39.8158 | 240 | 0.00030425 | 0.00030423 | 1.0952 | 240 | 44.4096 | 42.2754 | 240 | 6001.9396 | 1816.7682 | 3122.8471 | 883.6212
240 | 68.4 | 7 | 39.7897 | 0.00030424 | 240 | 4935.171 | 1524.3451 | 43.6765 | 3.2376 | 240 | 68.4 |  | 28.8 | 240 | 7 | 7 | 240 | 39.7897 | 39.756 | 240 | 0.00030424 | 0.00030425 | 1.0953 | 240 | 43.6765 | 41.2013 | 240 | 4935.171 | 1524.3451 | 1835.2918 | 575.4679
250 | 68.4 | 7 | 39.7897 | 0.00030424 | 250 | 4935.171 | 1524.3451 | 43.6765 | 3.2376 | 250 | 68.4 |  |  | 250 | 7 |  | 250 | 39.7897 |  | 250 | 0.00030424 |  |  | 250 | 43.6765 |  | 250 | 4935.171 | 1524.3451
250 | 58.2 | 7 | 39.6074 | 0.00030419 | 250 | 4404.4839 | 1264.1502 | 43.0768 | 3.4841 | 250 | 58.2 |  |  | 250 | 7 |  | 250 | 39.6074 |  | 250 | 0.00030419 |  |  | 250 | 43.0768 |  | 250 | 4404.4839 | 1264.1502
260 | 58.2 | 7 | 39.6074 | 0.00030419 | 260 | 4404.4839 | 1264.1502 | 43.0768 | 3.4841 | 260 | 58.2 |  |  | 260 | 7 |  | 260 | 39.6074 |  | 260 | 0.00030419 |  |  | 260 | 43.0768 |  | 260 | 4404.4839 | 1264.1502
260 | 48 | 7 | 39.6531 | 0.00030402 | 260 | 3474.675 | 979.8285 | 42.3916 | 3.5462 | 260 | 48 |  |  | 260 | 7 |  | 260 | 39.6531 |  | 260 | 0.00030402 |  |  | 260 | 42.3916 |  | 260 | 3474.675 | 979.8285
270 | 48 | 7 | 39.6531 | 0.00030402 | 270 | 3474.675 | 979.8285 | 42.3916 | 3.5462 | 270 | 48 |  |  | 270 | 7 |  | 270 | 39.6531 |  | 270 | 0.00030402 |  |  | 270 | 42.3916 |  | 270 | 3474.675 | 979.8285
270 | 42 | 7 | 39.8158 | 0.00030423 | 270 | 3122.8471 | 883.6212 | 42.2754 | 3.5341 | 270 | 42 |  |  | 270 | 7 |  | 270 | 39.8158 |  | 270 | 0.00030423 |  |  | 270 | 42.2754 |  | 270 | 3122.8471 | 883.6212
280 | 42 | 7 | 39.8158 | 0.00030423 | 280 | 3122.8471 | 883.6212 | 42.2754 | 3.5341 | 280 | 42 |  |  | 280 | 7 |  | 280 | 39.8158 |  | 280 | 0.00030423 |  |  | 280 | 42.2754 |  | 280 | 3122.8471 | 883.6212
280 | 28.8 | 7 | 39.756 | 0.00030425 | 280 | 1835.2918 | 575.4679 | 41.2013 | 3.1892 | 280 | 28.8 |  |  | 280 | 7 |  | 280 | 39.756 |  | 280 | 0.00030425 |  |  | 280 | 41.2013 |  | 280 | 1835.2918 | 575.4679
290 | 28.8 | 7 | 39.756 | 0.00030425 | 290 | 1835.2918 | 575.4679 | 41.2013 | 3.1892 | 290 | 28.8 |  |  | 290 | 7 |  | 290 | 39.756 |  | 290 | 0.00030425 |  |  | 290 | 41.2013 |  | 290 | 1835.2918 | 575.4679
290 | 105.6 | 2 | 29.2618 | 0.00032152 | 290 | 6804.1734 | 2157.9949 | 34.3325 | 3.153 | 290 | 105.6 |  | A2 W35 | 290 | 2 | A2 W35 | 290 | 29.2618 |  | 290 | 0.00032152 |  |  | 290 | 34.3325 |  | 290 | 6804.1734 | 2157.9949
300 | 105.6 | 2 | 29.2618 | 0.00032152 | 300 | 6804.1734 | 2157.9949 | 34.3325 | 3.153 | 300 | 105.6 |  | 105.6 | 300 | 2 | 2 | 300 | 29.2618 | 29.2618 | 300 | 0.00032152 | 0.00032152 | 1.1575 | 300 | 34.3325 | 34.3325 | 290 | 6804.1734 | 2157.9949 | 6804.1734 | 2157.9949
300 | 88.2 | 2 | 28.9635 | 0.00032128 | 300 | 6310.0376 | 1753.9105 | 33.6696 | 3.5977 | 300 | 88.2 |  | 88.2 | 300 | 2 | 2 | 300 | 28.9635 | 28.9635 | 300 | 0.00032128 | 0.00032128 | 1.1566 | 300 | 33.6696 | 33.6696 | 300 | 6310.0376 | 1753.9105 | 6310.0376 | 1753.9105
310 | 88.2 | 2 | 28.9635 | 0.00032128 | 310 | 6310.0376 | 1753.9105 | 33.6696 | 3.5977 | 310 | 88.2 |  | 68.4 | 310 | 2 | 2 | 310 | 28.9635 | 31.3334 | 310 | 0.00032128 | 0.00032107 | 1.1559 | 310 | 33.6696 | 34.5005 | 300 | 6310.0376 | 1753.9105 | 4243.8366 | 1252.1499
310 | 68.4 | 2 | 31.3334 | 0.00032107 | 310 | 4243.8366 | 1252.1499 | 34.5005 | 3.3892 | 310 | 68.4 |  | 48 | 310 | 2 | 2 | 310 | 31.3334 | 32.0701 | 310 | 0.00032107 | 0.00032093 | 1.1554 | 310 | 34.5005 | 34.665 | 310 | 4243.8366 | 1252.1499 | 3475.5644 | 892.6959
320 | 68.4 | 2 | 31.3334 | 0.00032107 | 320 | 4243.8366 | 1252.1499 | 34.5005 | 3.3892 | 320 | 68.4 |  | 28.8 | 320 | 2 | 2 | 320 | 31.3334 | 33.3875 | 320 | 0.00032107 | 0.00032065 | 1.1543 | 320 | 34.5005 | 34.6744 | 310 | 4243.8366 | 1252.1499 | 1722.0681 | 499.3726
320 | 48 | 2 | 32.0701 | 0.00032093 | 320 | 3475.5644 | 892.6959 | 34.665 | 3.8933 | 320 | 48 |  |  | 320 | 2 |  | 320 | 32.0701 |  | 320 | 0.00032093 |  |  | 320 | 34.665 |  | 320 | 3475.5644 | 892.6959
330 | 48 | 2 | 32.0701 | 0.00032093 | 330 | 3475.5644 | 892.6959 | 34.665 | 3.8933 | 330 | 48 |  |  | 330 | 2 |  | 330 | 32.0701 |  | 330 | 0.00032093 |  |  | 330 | 34.665 |  | 320 | 3475.5644 | 892.6959
330 | 28.8 | 2 | 33.3875 | 0.00032065 | 330 | 1722.0681 | 499.3726 | 34.6744 | 3.4485 | 330 | 28.8 |  |  | 330 | 2 |  | 330 | 33.3875 |  | 330 | 0.00032065 |  |  | 330 | 34.6744 |  | 330 | 1722.0681 | 499.3726
340 | 28.8 | 2 | 33.3875 | 0.00032065 | 340 | 1722.0681 | 499.3726 | 34.6744 | 3.4485 | 340 | 28.8 |  |  | 340 | 2 |  | 340 | 33.3875 |  | 340 | 0.00032065 |  |  | 340 | 34.6744 |  | 330 | 1722.0681 | 499.3726
340 | 105.6 | 2 | 40.3872 | 0.00030085 | 340 | 6058.7964 | 2511.6478 | 45.2127 | 2.4123 | 340 | 105.6 |  | A2 W45 | 340 | 2 | A2 W45 | 340 | 40.3872 |  | 340 | 0.00030085 |  |  | 340 | 45.2127 |  | 340 | 6058.7964 | 2511.6478
350 | 105.6 | 2 | 40.3872 | 0.00030085 | 350 | 6058.7964 | 2511.6478 | 45.2127 | 2.4123 | 350 | 105.6 |  | 105.6 | 350 | 2 | 2 | 350 | 40.3872 | 40.3872 | 350 | 0.00030085 | 0.00030085 | 1.083 | 350 | 45.2127 | 45.2127 | 340 | 6058.7964 | 2511.6478 | 6058.7964 | 2511.6478
350 | 88.2 | 2 | 40.204 | 0.00030358 | 350 | 5198.6167 | 2031.8338 | 44.3073 | 2.5586 | 350 | 88.2 |  | 88.2 | 350 | 2 | 2 | 350 | 40.204 | 40.204 | 350 | 0.00030358 | 0.00030358 | 1.0929 | 350 | 44.3073 | 44.3073 | 350 | 5198.6167 | 2031.8338 | 5198.6167 | 2031.8338
360 | 88.2 | 2 | 40.204 | 0.00030358 | 360 | 5198.6167 | 2031.8338 | 44.3073 | 2.5586 | 360 | 88.2 |  | 68.4 | 360 | 2 | 2 | 360 | 40.204 | 40.2287 | 360 | 0.00030358 | 0.00030341 | 1.0923 | 360 | 44.3073 | 43.4444 | 350 | 5198.6167 | 2031.8338 | 4071.8312 | 1516.4586
360 | 68.4 | 2 | 40.2287 | 0.00030341 | 360 | 4071.8312 | 1516.4586 | 43.4444 | 2.6851 | 360 | 68.4 |  | 48 | 360 | 2 | 2 | 360 | 40.2287 | 40.467 | 360 | 0.00030341 | 0.0003037 | 1.0933 | 360 | 43.4444 | 42.9388 | 360 | 4071.8312 | 1516.4586 | 3132.9614 | 1063.8925
370 | 68.4 | 2 | 40.2287 | 0.00030341 | 370 | 4071.8312 | 1516.4586 | 43.4444 | 2.6851 | 370 | 68.4 |  | 28.8 | 370 | 2 | 2 | 370 | 40.2287 | 43.5058 | 370 | 0.00030341 | 0.00030367 | 1.0932 | 370 | 43.4444 | 44.6452 | 360 | 4071.8312 | 1516.4586 | 1443.9843 | 633.0049
370 | 48 | 2 | 40.467 | 0.0003037 | 370 | 3132.9614 | 1063.8925 | 42.9388 | 2.9448 | 370 | 48 |  |  | 370 | 2 |  | 370 | 40.467 |  | 370 | 0.0003037 |  |  | 370 | 42.9388 |  | 370 | 3132.9614 | 1063.8925
380 | 48 | 2 | 40.467 | 0.0003037 | 380 | 3132.9614 | 1063.8925 | 42.9388 | 2.9448 | 380 | 48 |  |  | 380 | 2 |  | 380 | 40.467 |  | 380 | 0.0003037 |  |  | 380 | 42.9388 |  | 370 | 3132.9614 | 1063.8925
380 | 28.8 | 2 | 43.5058 | 0.00030367 | 380 | 1443.9843 | 633.0049 | 44.6452 | 2.2812 | 380 | 28.8 |  |  | 380 | 2 |  | 380 | 43.5058 |  | 380 | 0.00030367 |  |  | 380 | 44.6452 |  | 380 | 1443.9843 | 633.0049
390 | 28.8 | 2 | 43.5058 | 0.00030367 | 390 | 1443.9843 | 633.0049 | 44.6452 | 2.2812 | 390 | 28.8 |  |  | 390 | 2 |  | 390 | 43.5058 |  | 390 | 0.00030367 |  |  | 390 | 44.6452 |  | 380 | 1443.9843 | 633.0049
390 | 105.6 | 2 | 48.6932 | 0.0001898 | 390 | 4443.0697 | 2414.3846 | 54.3024 | 1.8402 | 390 | 105.6 |  | A2 W55 | 390 | 2 | A2 W55 | 390 | 48.6932 |  | 390 | 0.0001898 |  |  | 390 | 54.3024 |  | 390 | 4443.0697 | 2414.3846
400 | 105.6 | 2 | 48.6932 | 0.0001898 | 400 | 4443.0697 | 2414.3846 | 54.3024 | 1.8402 | 400 | 105.6 |  | 105.6 | 400 | 2 | 2 | 400 | 48.6932 | 48.6932 | 400 | 0.0001898 | 0.0001898 | 0.68327 | 400 | 54.3024 | 54.3024 | 390 | 4443.0697 | 2414.3846 | 4443.0697 | 2414.3846
400 | 88.2 | 2 | 48.5409 | 0.00018914 | 400 | 4293.3593 | 2294.2294 | 53.9797 | 1.8714 | 400 | 88.2 |  | 88.2 | 400 | 2 | 2 | 400 | 48.5409 | 48.5409 | 400 | 0.00018914 | 0.00018914 | 0.68092 | 400 | 53.9797 | 53.9797 | 400 | 4293.3593 | 2294.2294 | 4293.3593 | 2294.2294
410 | 88.2 | 2 | 48.5409 | 0.00018914 | 410 | 4293.3593 | 2294.2294 | 53.9797 | 1.8714 | 410 | 88.2 |  | 68.4 | 410 | 2 | 2 | 410 | 48.5409 | 48.6104 | 410 | 0.00018914 | 0.00018928 | 0.68139 | 410 | 53.9797 | 53.5211 | 400 | 4293.3593 | 2294.2294 | 3879.1158 | 1835.9497
410 | 68.4 | 2 | 48.6104 | 0.00018928 | 410 | 3879.1158 | 1835.9497 | 53.5211 | 2.1129 | 410 | 68.4 |  | 48 | 410 | 2 | 2 | 410 | 48.6104 | 48.6163 | 410 | 0.00018928 | 0.00018889 | 0.68 | 410 | 53.5211 | 52.2043 | 410 | 3879.1158 | 1835.9497 | 2828.4204 | 1260.9779
420 | 68.4 | 2 | 48.6104 | 0.00018928 | 420 | 3879.1158 | 1835.9497 | 53.5211 | 2.1129 | 420 | 68.4 |  | 28.8 | 420 | 2 | 2 | 420 | 48.6104 | 48.6497 | 420 | 0.00018928 | 0.00018906 | 0.68063 | 420 | 53.5211 | 50.3293 | 410 | 3879.1158 | 1835.9497 | 1325.3079 | 752.9151
420 | 48 | 2 | 48.6163 | 0.00018889 | 420 | 2828.4204 | 1260.9779 | 52.2043 | 2.243 | 420 | 48 |  |  | 420 | 2 |  | 420 | 48.6163 |  | 420 | 0.00018889 |  |  | 420 | 52.2043 |  | 420 | 2828.4204 | 1260.9779
430 | 48 | 2 | 48.6163 | 0.00018889 | 430 | 2828.4204 | 1260.9779 | 52.2043 | 2.243 | 430 | 48 |  |  | 430 | 2 |  | 430 | 48.6163 |  | 430 | 0.00018889 |  |  | 430 | 52.2043 |  | 420 | 2828.4204 | 1260.9779
430 | 28.8 | 2 | 48.6497 | 0.00018906 | 430 | 1325.3079 | 752.9151 | 50.3293 | 1.7602 | 430 | 28.8 |  |  | 430 | 2 |  | 430 | 48.6497 |  | 430 | 0.00018906 |  |  | 430 | 50.3293 |  | 430 | 1325.3079 | 752.9151
440 | 28.8 | 2 | 48.6497 | 0.00018906 | 440 | 1325.3079 | 752.9151 | 50.3293 | 1.7602 | 440 | 28.8 |  |  | 440 | 2 |  | 440 | 48.6497 |  | 440 | 0.00018906 |  |  | 440 | 50.3293 |  | 430 | 1325.3079 | 752.9151
440 | 105.6 | -7 | 30.5762 | 0.00032102 | 440 | 4922.2233 | 1958.9899 | 34.2502 | 2.5126 | 440 | 105.6 |  | A-7 W35 | 440 | -7 | A-7 W35 | 440 | 30.5762 |  | 440 | 0.00032102 |  |  | 440 | 34.2502 |  | 440 | 4922.2233 | 1958.9899
450 | 105.6 | -7 | 30.5762 | 0.00032102 | 450 | 4922.2233 | 1958.9899 | 34.2502 | 2.5126 | 450 | 105.6 |  | 105.6 | 450 | -7 | -7 | 450 | 30.5762 | 30.5762 | 450 | 0.00032102 | 0.00032102 | 1.1557 | 450 | 34.2502 | 34.2502 | 440 | 4922.2233 | 1958.9899 | 4922.2233 | 1958.9899
450 | 88.2 | -7 | 30.6649 | 0.00032091 | 450 | 4297.8099 | 1599.147 | 33.8739 | 2.6876 | 450 | 88.2 |  | 88.2 | 450 | -7 | -7 | 450 | 30.6649 | 30.6649 | 450 | 0.00032091 | 0.00032091 | 1.1553 | 450 | 33.8739 | 33.8739 | 450 | 4297.8099 | 1599.147 | 4297.8099 | 1599.147
460 | 88.2 | -7 | 30.6649 | 0.00032091 | 460 | 4297.8099 | 1599.147 | 33.8739 | 2.6876 | 460 | 88.2 |  | 68.4 | 460 | -7 | -7 | 460 | 30.6649 | 30.5143 | 460 | 0.00032091 | 0.00032089 | 1.1552 | 460 | 33.8739 | 32.9842 | 450 | 4297.8099 | 1599.147 | 3307.7116 | 1187.6682
460 | 68.4 | -7 | 30.5143 | 0.00032089 | 460 | 3307.7116 | 1187.6682 | 32.9842 | 2.785 | 460 | 68.4 |  | 48 | 460 | -7 | -7 | 460 | 30.5143 | 30.6035 | 460 | 0.00032089 | 0.00032096 | 1.1555 | 460 | 32.9842 | 32.4422 | 460 | 3307.7116 | 1187.6682 | 2462.9423 | 822.4511
470 | 68.4 | -7 | 30.5143 | 0.00032089 | 470 | 3307.7116 | 1187.6682 | 32.9842 | 2.785 | 470 | 68.4 |  | 28.8 | 470 | -7 | -7 | 470 | 30.5143 | 30.597 | 470 | 0.00032089 | 0.00032087 | 1.1551 | 470 | 32.9842 | 31.6023 | 460 | 3307.7116 | 1187.6682 | 1346.2666 | 531.3308
470 | 48 | -7 | 30.6035 | 0.00032096 | 470 | 2462.9423 | 822.4511 | 32.4422 | 2.9946 | 470 | 48 |  |  | 470 | -7 |  | 470 | 30.6035 |  | 470 | 0.00032096 |  |  | 470 | 32.4422 |  | 470 | 2462.9423 | 822.4511
480 | 48 | -7 | 30.6035 | 0.00032096 | 480 | 2462.9423 | 822.4511 | 32.4422 | 2.9946 | 480 | 48 |  |  | 480 | -7 |  | 480 | 30.6035 |  | 480 | 0.00032096 |  |  | 480 | 32.4422 |  | 470 | 2462.9423 | 822.4511
480 | 28.8 | -7 | 30.597 | 0.00032087 | 480 | 1346.2666 | 531.3308 | 31.6023 | 2.5338 | 480 | 28.8 |  |  | 480 | -7 |  | 480 | 30.597 |  | 480 | 0.00032087 |  |  | 480 | 31.6023 |  | 480 | 1346.2666 | 531.3308
490 | 28.8 | -7 | 30.597 | 0.00032087 | 490 | 1346.2666 | 531.3308 | 31.6023 | 2.5338 | 490 | 28.8 |  |  | 490 | -7 |  | 490 | 30.597 |  | 490 | 0.00032087 |  |  | 490 | 31.6023 |  | 480 | 1346.2666 | 531.3308
490 | 105.6 | -7 | 40.9822 | 0.00030671 | 490 | 4716.8698 | 2380.2043 | 44.6671 | 1.9817 | 490 | 105.6 |  | A-7 W45 | 490 | -7 | A-7 W45 | 490 | 40.9822 |  | 490 | 0.00030671 |  |  | 490 | 44.6671 |  | 490 | 4716.8698 | 2380.2043
500 | 105.6 | -7 | 40.9822 | 0.00030671 | 500 | 4716.8698 | 2380.2043 | 44.6671 | 1.9817 | 500 | 105.6 |  | 105.6 | 500 | -7 | -7 | 500 | 40.9822 | 40.9822 | 500 | 0.00030671 | 0.00030671 | 1.1042 | 500 | 44.6671 | 44.6671 | 490 | 4716.8698 | 2380.2043 | 4716.8698 | 2380.2043
500 | 88.2 | -7 | 40.6645 | 0.00030361 | 500 | 3955.1349 | 1911.4088 | 43.7859 | 2.0692 | 500 | 88.2 |  | 88.2 | 500 | -7 | -7 | 500 | 40.6645 | 40.6645 | 500 | 0.00030361 | 0.00030361 | 1.093 | 500 | 43.7859 | 43.7859 | 500 | 3955.1349 | 1911.4088 | 3955.1349 | 1911.4088
510 | 88.2 | -7 | 40.6645 | 0.00030361 | 510 | 3955.1349 | 1911.4088 | 43.7859 | 2.0692 | 510 | 88.2 |  | 68.4 | 510 | -7 | -7 | 510 | 40.6645 | 40.753 | 510 | 0.00030361 | 0.00030363 | 1.0931 | 510 | 43.7859 | 43.2114 | 500 | 3955.1349 | 1911.4088 | 3115.2881 | 1436.1389
510 | 68.4 | -7 | 40.753 | 0.00030363 | 510 | 3115.2881 | 1436.1389 | 43.2114 | 2.1692 | 510 | 68.4 |  | 48 | 510 | -7 | -7 | 510 | 40.753 | 40.77 | 510 | 0.00030363 | 0.00030353 | 1.0927 | 510 | 43.2114 | 42.4755 | 510 | 3115.2881 | 1436.1389 | 2160.3795 | 1009.1906
520 | 68.4 | -7 | 40.753 | 0.00030363 | 520 | 3115.2881 | 1436.1389 | 43.2114 | 2.1692 | 520 | 68.4 |  | 28.8 | 520 | -7 | -7 | 520 | 40.753 | 40.7244 | 520 | 0.00030363 | 0.00030357 | 1.0928 | 520 | 43.2114 | 41.4543 | 510 | 3115.2881 | 1436.1389 | 924.6794 | 633.0724
520 | 48 | -7 | 40.77 | 0.00030353 | 520 | 2160.3795 | 1009.1906 | 42.4755 | 2.1407 | 520 | 48 |  |  | 520 | -7 |  | 520 | 40.77 |  | 520 | 0.00030353 |  |  | 520 | 42.4755 |  | 520 | 2160.3795 | 1009.1906
530 | 48 | -7 | 40.77 | 0.00030353 | 530 | 2160.3795 | 1009.1906 | 42.4755 | 2.1407 | 530 | 48 |  |  | 530 | -7 |  | 530 | 40.77 |  | 530 | 0.00030353 |  |  | 530 | 42.4755 |  | 520 | 2160.3795 | 1009.1906
530 | 28.8 | -7 | 40.7244 | 0.00030357 | 530 | 924.6794 | 633.0724 | 41.4543 | 1.4606 | 530 | 28.8 |  |  | 530 | -7 |  | 530 | 40.7244 |  | 530 | 0.00030357 |  |  | 530 | 41.4543 |  | 530 | 924.6794 | 633.0724
540 | 28.8 | -7 | 40.7244 | 0.00030357 | 540 | 924.6794 | 633.0724 | 41.4543 | 1.4606 | 540 | 28.8 |  |  | 540 | -7 |  | 540 | 40.7244 |  | 540 | 0.00030357 |  |  | 540 | 41.4543 |  | 530 | 924.6794 | 633.0724

## DATA 1 NO DEFROST
Compr_freq |  |  |  | Tair |  |  | Twater |  |  | Qwater |  |  |  | y_HP_Power | y_Power_All
Time | [Hz] | A12 W35 | Time | [°C] |  | Time | [°C] |  | Time | [m3/s] | [m3/s] | [m3/h] | Time | Tair
0 | 105.6 | 105.6 | 0 | 12 | 12 | 0 | 30.1128 | 30.1128 | 0 | 0.00041469 | 0.00041469 | 1.4929 | 0 | 8628.7753 | 2022.2983 | 8628.7753 | 2022.2983
1 | 105.6 | 98.4 | 1 | 12 | 12 | 1 | 30.1128 | 30.139 | 1 | 0.00041469 | 0.00040901 | 1.4725 | 1 | 8628.7753 | 2022.2983 | 8589.4443 | 2044.1492
1 | 98.4 | 88.2 | 1 | 12 | 12 | 1 | 30.139 | 30.0812 | 1 | 0.00040901 | 0.00037003 | 1.3321 | 1 | 8589.4443 | 2044.1492 | 7641.7973 | 1748.7238
2 | 98.4 | 78 | 2 | 12 | 12 | 2 | 30.139 | 30.2097 | 2 | 0.00040901 | 0.00033553 | 1.2079 | 2 | 8589.4443 | 2044.1492 | 6873.7837 | 1477.2597
2 | 88.2 | 68.4 | 2 | 12 | 12 | 2 | 30.0812 | 30.0961 | 2 | 0.00037003 | 0.0002919 | 1.0508 | 2 | 7641.7973 | 1748.7238 | 6035.4402 | 1248.4972
3 | 88.2 | 58.2 | 3 | 12 | 12 | 3 | 30.0812 | 30.1272 | 3 | 0.00037003 | 0.00027116 | 0.97619 | 3 | 7641.7973 | 1748.7238 | 5577.8223 | 1050.5967
3 | 78 | 48 | 3 | 12 | 12 | 3 | 30.2097 | 30.1258 | 3 | 0.00033553 | 0.00022044 | 0.79358 | 3 | 6873.7837 | 1477.2597 | 4599.0189 | 834.9834
4 | 78 | 42 | 4 | 12 | 12 | 4 | 30.2097 | 30.0702 | 4 | 0.00033553 | 0.00017488 | 0.62956 | 4 | 6873.7837 | 1477.2597 | 3688.431 | 632.2928
4 | 68.4 | 28.8 | 4 | 12 | 12 | 4 | 30.0961 | 30.0828 | 4 | 0.0002919 | 0.00012753 | 0.45911 | 4 | 6035.4402 | 1248.4972 | 2697.5201 | 467.2762
5 | 68.4 |  | 5 | 12 |  | 5 | 30.0961 |  | 5 | 0.0002919 |  |  | 5 | 6035.4402 | 1248.4972
5 | 58.2 |  | 5 | 12 |  | 5 | 30.1272 |  | 5 | 0.00027116 |  |  | 5 | 5577.8223 | 1050.5967
6 | 58.2 |  | 6 | 12 |  | 6 | 30.1272 |  | 6 | 0.00027116 |  |  | 6 | 5577.8223 | 1050.5967
6 | 48 |  | 6 | 12 |  | 6 | 30.1258 |  | 6 | 0.00022044 |  |  | 6 | 4599.0189 | 834.9834
7 | 48 |  | 7 | 12 |  | 7 | 30.1258 |  | 7 | 0.00022044 |  |  | 7 | 4599.0189 | 834.9834
7 | 42 |  | 7 | 12 |  | 7 | 30.0702 |  | 7 | 0.00017488 |  |  | 7 | 3688.431 | 632.2928
8 | 42 |  | 8 | 12 |  | 8 | 30.0702 |  | 8 | 0.00017488 |  |  | 8 | 3688.431 | 632.2928
8 | 28.8 |  | 8 | 12 |  | 8 | 30.0828 |  | 8 | 0.00012753 |  |  | 8 | 2697.5201 | 467.2762
9 | 28.8 | A12 W45 | 9 | 12 |  | 9 | 30.0828 |  | 9 | 0.00012753 | [m3/s] | [m3/h] | 9 | 2697.5201 | 467.2762
9 | 98.4 | 98.4 | 9 | 12 | 12 | 9 | 40.0941 | 40.0941 | 9 | 0.00033785 | 0.00033785 | 1.2163 | 9 | 7107.439 | 2038.0663 | 7107.439 | 2038.0663
10 | 98.4 | 88.2 | 10 | 12 | 12 | 10 | 40.0941 | 40.0885 | 10 | 0.00033785 | 0.00034099 | 1.2276 | 10 | 7107.439 | 2038.0663 | 7067.6887 | 2021.3591
10 | 88.2 | 78 | 10 | 12 | 12 | 10 | 40.0885 | 40.0682 | 10 | 0.00034099 | 0.0003224 | 1.1606 | 10 | 7067.6887 | 2021.3591 | 6699.1561 | 1829.7901
11 | 88.2 | 68.4 | 11 | 12 | 12 | 11 | 40.0885 | 40.1126 | 11 | 0.00034099 | 0.00027957 | 1.0064 | 11 | 7067.6887 | 2021.3591 | 5769.3496 | 1543.0276
11 | 78 | 58.2 | 11 | 12 | 12 | 11 | 40.0682 | 40.0896 | 11 | 0.0003224 | 0.00025498 | 0.91793 | 11 | 6699.1561 | 1829.7901 | 5336.9388 | 1301.1768
12 | 78 | 48 | 12 | 12 | 12 | 12 | 40.0682 | 40.0435 | 12 | 0.0003224 | 0.00020553 | 0.73991 | 12 | 6699.1561 | 1829.7901 | 4219.4372 | 1060.1436
12 | 68.4 | 42 | 12 | 12 | 12 | 12 | 40.1126 | 40.0775 | 12 | 0.00027957 | 0.0001626 | 0.58534 | 12 | 5769.3496 | 1543.0276 | 3290.2776 | 815.0166
13 | 68.4 | 28.8 | 13 | 12 | 12 | 13 | 40.1126 | 39.924 | 13 | 0.00027957 | 0.00016401 | 0.59043 | 13 | 5769.3496 | 1543.0276 | 2338.7102 | 589.7238
13 | 58.2 |  | 13 | 12 |  | 13 | 40.0896 |  | 13 | 0.00025498 |  |  | 13 | 5336.9388 | 1301.1768
14 | 58.2 |  | 14 | 12 |  | 14 | 40.0896 |  | 14 | 0.00025498 |  |  | 14 | 5336.9388 | 1301.1768
14 | 48 |  | 14 | 12 |  | 14 | 40.0435 |  | 14 | 0.00020553 |  |  | 14 | 4219.4372 | 1060.1436
15 | 48 |  | 15 | 12 |  | 15 | 40.0435 |  | 15 | 0.00020553 |  |  | 15 | 4219.4372 | 1060.1436
15 | 42 |  | 15 | 12 |  | 15 | 40.0775 |  | 15 | 0.0001626 |  |  | 15 | 3290.2776 | 815.0166
16 | 42 |  | 16 | 12 |  | 16 | 40.0775 |  | 16 | 0.0001626 |  |  | 16 | 3290.2776 | 815.0166
16 | 28.8 |  | 16 | 12 |  | 16 | 39.924 |  | 16 | 0.00016401 |  |  | 16 | 2338.7102 | 589.7238
17 | 28.8 | A12 W35 | 17 | 12 |  | 17 | 39.924 |  | 17 | 0.00016401 |  |  | 17 | 2338.7102 | 589.7238
17 | 86.4 | 86.4 | 17 | 7 | 7 | 17 | 29.7349 | 29.7349 | 17 | 0.00032274 | 0.00032274 | 1.1619 | 17 | 6462.1145 | 1508.1757 | 6462.1145 | 1508.1757
18 | 86.4 | 78 | 18 | 7 | 7 | 18 | 29.7349 | 29.7576 | 18 | 0.00032274 | 0.00032273 | 1.1618 | 18 | 6462.1145 | 1508.1757 | 6298.4762 | 1433.1706
18 | 78 | 68.4 | 18 | 7 | 7 | 18 | 29.7576 | 30.4659 | 18 | 0.00032273 | 0.0003217 | 1.1581 | 18 | 6298.4762 | 1433.1706 | 5626.8987 | 1260.8976
19 | 78 | 68.4 | 19 | 7 | 7 | 19 | 29.7576 | 29.7427 | 19 | 0.00032273 | 0.00032257 | 1.1613 | 19 | 6298.4762 | 1433.1706 | 5556.9219 | 1202.3305
19 | 68.4 | 58.2 | 19 | 7 | 7 | 19 | 30.4659 | 30.4464 | 19 | 0.0003217 | 0.00032161 | 1.1578 | 19 | 5626.8987 | 1260.8976 | 5038.1029 | 1046.0134
20 | 68.4 | 48 | 20 | 7 | 7 | 20 | 30.4659 | 30.4595 | 20 | 0.0003217 | 0.00032162 | 1.1578 | 20 | 5626.8987 | 1260.8976 | 4132.5819 | 823.5499
20 | 68.4 | 42 | 20 | 7 | 7 | 20 | 29.7427 | 30.4868 | 20 | 0.00032257 | 0.00032149 | 1.1574 | 20 | 5556.9219 | 1202.3305 | 3660.7586 | 706.1911
21 | 68.4 | 28.8 | 21 | 7 | 7 | 21 | 29.7427 | 30.5336 | 21 | 0.00032257 | 0.00032133 | 1.1568 | 21 | 5556.9219 | 1202.3305 | 2528.7339 | 461.1996
21 | 58.2 |  | 21 | 7 |  | 21 | 30.4464 |  | 21 | 0.00032161 |  |  | 21 | 5038.1029 | 1046.0134
22 | 58.2 |  | 22 | 7 |  | 22 | 30.4464 |  | 22 | 0.00032161 |  |  | 22 | 5038.1029 | 1046.0134
22 | 48 |  | 22 | 7 |  | 22 | 30.4595 |  | 22 | 0.00032162 |  |  | 22 | 4132.5819 | 823.5499
23 | 48 |  | 23 | 7 |  | 23 | 30.4595 |  | 23 | 0.00032162 |  |  | 23 | 4132.5819 | 823.5499
23 | 42 |  | 23 | 7 |  | 23 | 30.4868 |  | 23 | 0.00032149 |  |  | 23 | 3660.7586 | 706.1911
24 | 42 |  | 24 | 7 |  | 24 | 30.4868 |  | 24 | 0.00032149 |  |  | 24 | 3660.7586 | 706.1911
24 | 28.8 |  | 24 | 7 |  | 24 | 30.5336 |  | 24 | 0.00032133 |  |  | 24 | 2528.7339 | 461.1996
25 | 28.8 | A7 W45 | 25 | 7 |  | 25 | 30.5336 |  | 25 | 0.00032133 |  |  | 25 | 2528.7339 | 461.1996
25 | 93 | 93 | 25 | 7 | 7 | 25 | 39.721 | 39.721 | 25 | 0.00030123 | 0.00030123 | 1.0844 | 25 | 7136.8048 | 2350.8678 | 7136.8048 | 2350.8678
26 | 93 | 88.2 | 26 | 7 | 7 | 26 | 39.721 | 39.645 | 26 | 0.00030123 | 0.00030412 | 1.0948 | 26 | 7136.8048 | 2350.8678 | 6722.4482 | 2149.2013
26 | 88.2 | 86.4 | 26 | 7 | 7 | 26 | 39.645 | 39.7455 | 26 | 0.00030412 | 0.00030426 | 1.0953 | 26 | 6722.4482 | 2149.2013 | 6610.7237 | 2102.8202
27 | 88.2 | 78 | 27 | 7 | 7 | 27 | 39.645 | 39.6828 | 27 | 0.00030412 | 0.00030425 | 1.0953 | 27 | 6722.4482 | 2149.2013 | 6001.9396 | 1816.7682
27 | 86.4 | 68.4 | 27 | 7 | 7 | 27 | 39.7455 | 39.7897 | 27 | 0.00030426 | 0.00030424 | 1.0953 | 27 | 6610.7237 | 2102.8202 | 4935.171 | 1524.3451
28 | 86.4 | 58.2 | 28 | 7 | 7 | 28 | 39.7455 | 39.6074 | 28 | 0.00030426 | 0.00030419 | 1.0951 | 28 | 6610.7237 | 2102.8202 | 4404.4839 | 1264.1502
28 | 78 | 48 | 28 | 7 | 7 | 28 | 39.6828 | 39.6531 | 28 | 0.00030425 | 0.00030402 | 1.0945 | 28 | 6001.9396 | 1816.7682 | 3474.675 | 979.8285
29 | 78 | 42 | 29 | 7 | 7 | 29 | 39.6828 | 39.8158 | 29 | 0.00030425 | 0.00030423 | 1.0952 | 29 | 6001.9396 | 1816.7682 | 3122.8471 | 883.6212
29 | 68.4 | 28.8 | 29 | 7 | 7 | 29 | 39.7897 | 39.756 | 29 | 0.00030424 | 0.00030425 | 1.0953 | 29 | 4935.171 | 1524.3451 | 1835.2918 | 575.4679
30 | 68.4 |  | 30 | 7 |  | 30 | 39.7897 |  | 30 | 0.00030424 |  |  | 30 | 4935.171 | 1524.3451
30 | 58.2 |  | 30 | 7 |  | 30 | 39.6074 |  | 30 | 0.00030419 |  |  | 30 | 4404.4839 | 1264.1502
31 | 58.2 |  | 31 | 7 |  | 31 | 39.6074 |  | 31 | 0.00030419 |  |  | 31 | 4404.4839 | 1264.1502
31 | 48 |  | 31 | 7 |  | 31 | 39.6531 |  | 31 | 0.00030402 |  |  | 31 | 3474.675 | 979.8285
32 | 48 |  | 32 | 7 |  | 32 | 39.6531 |  | 32 | 0.00030402 |  |  | 32 | 3474.675 | 979.8285
32 | 42 |  | 32 | 7 |  | 32 | 39.8158 |  | 32 | 0.00030423 |  |  | 32 | 3122.8471 | 883.6212
33 | 42 |  | 33 | 7 |  | 33 | 39.8158 |  | 33 | 0.00030423 |  |  | 33 | 3122.8471 | 883.6212
33 | 28.8 |  | 33 | 7 |  | 33 | 39.756 |  | 33 | 0.00030425 |  |  | 33 | 1835.2918 | 575.4679
34 | 28.8 |  | 34 | 7 |  | 34 | 39.756 |  | 34 | 0.00030425 |  |  | 34 | 1835.2918 | 575.4679
34 | 105.6 | A7 W55 | 34 | 7 |  | 34 | 49.3668 |  | 34 | 0.00027814 |  |  | 34 | 5803.6858 | 2558.6461
35 | 105.6 | 105.6 | 35 | 7 | 7 | 35 | 49.3668 | 49.3668 | 35 | 0.00027814 | 0.00027814 | 1.0013 | 35 | 5803.6858 | 2558.6461 | 5803.6858 | 2558.6461
35 | 103.2 | 103.2 | 35 | 7 | 7 | 35 | 49.6627 | 49.6627 | 35 | 0.00029318 | 0.00029318 | 1.0555 | 35 | 5526.4081 | 2416.7833 | 5526.4081 | 2416.7833
36 | 103.2 | 98.4 | 36 | 7 | 7 | 36 | 49.6627 | 49.649 | 36 | 0.00029318 | 0.00029322 | 1.0556 | 36 | 5526.4081 | 2416.7833 | 5530.4565 | 2405.2069
36 | 98.4 | 68.4 | 36 | 7 | 7 | 36 | 49.649 | 49.4504 | 36 | 0.00029322 | 0.0002932 | 1.0555 | 36 | 5530.4565 | 2405.2069 | 4387.6718 | 1713.6534
37 | 98.4 |  | 37 | 7 |  | 37 | 49.649 |  | 37 | 0.00029322 |  |  | 37 | 5530.4565 | 2405.2069
37 | 68.4 |  | 37 | 7 |  | 37 | 49.4504 |  | 37 | 0.0002932 |  |  | 37 | 4387.6718 | 1713.6534
38 | 68.4 |  | 38 | 7 |  | 38 | 49.4504 |  | 38 | 0.0002932 |  |  | 38 | 4387.6718 | 1713.6534

## DATA fan
| HEATING | [11 empty] | COOLING
|  | Compressor speed [Hz] | [12 empty] | Compressor speed [Hz]
| Fan speed [RPM] | 16.8 | 47.9 | 48.5 | T0 ¦°C] | 16.8 | 47.899 | 47.9 | 48.499 | 48.5 | 130 |  |  | Fan speed [RPM] | 13.8 |  | 31.7 |  | 32.3 |  | T0 ¦°C] | 13.8 | 31.699 | 31.7 | 32.299 | 32.3 | 130
T0 | To ≥ 15°C | 6.1667 | 10 | 10 | 15 | 6.1667 | 6.1667 | 10 | 10 | 10 | 10 |  | T0 | To ≥ 38°C | 5 | 6.1667 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 38 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 11.6667
| To < 15°C | 6.1667 | 10 | 10 | 15 | 6.1667 | 6.1667 | 10 | 10 | 10 | 10 |  |  | To ≥ 28°C | 5 | 6.1667 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 28 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 11.6667
| To < 5.5°C | 10 | 10 | 11.6667 | 5.5 | 10 | 10 | 11.6667 | 11.6667 | 11.6667 | 11.6667 |  |  | To ≥ 15°C | 5 | 6.1667 | 9.1667 | 10 | 10 | 11.6667 | 15 | 10 | 10 | 11.6667 | 11.6667 | 11.6667 | 11.6667
| To < - 5.0°C | 10.8333 | 11.6667 | 11.6667 | -5 | 10.8333 | 10.8333 | 11.6667 | 11.6667 | 11.6667 | 11.6667 |  |  | To ≥ 5.5°C | 3.3333 | 6.1667 | 5 | 7.3333 | 7.3333 | 9.1667 | 5.5 | 7.3333 | 7.3333 | 9.1667 | 9.1667 | 9.1667 | 9.1667
| To ≥ 15°C | 6.1667 | 6.1667 | 8.3333 | [9 empty] | To ≥ 0°C | 3.3333 | 3.3333 | 3.3333 | 5 | 5 | 7.3333 | 0 | 5 | 5 | 7.3333 | 7.3333 | 7.3333 | 7.3333
| To < 15°C | 6.1667 | 6.1667 | 10 | [9 empty] | To < 0°C | 0 | 0 | 0 | 3.3333 | 3.3333 | 5
| To < 5.5°C | 7.3333 | 10 | 10 | [8 empty] | ECO mode | To ≥ 38°C | 5 | 6.1667 | 10.8333 | 11.6667 | 11.6667 | 11.6667
| To < - 5.5°C | 9.1667 | 10 | 10.8333 | [9 empty] | To < 38°C | 5 | 6.1667 | 5 | 6.1667 | 10.8333 | 11.6667
T0 abnormal |  | 10 | 10.8333 | 11.6667 | [8 empty] | T0 abnormal |  | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 11.6667 | 11.6667
Fan speed Reference [Hz]
Tap | GM30 | Tap | GM30
f 0 | 0 | f 9 | 10
f 1 | 3.3333 | f A | 10
f 2 | 5 | f B | 10.8333 | [8 empty] | -160 | 16.8 | 47.9 | 48.5 | 150
f 3 | 6.1667 | f C | 11.6667 | [8 empty] | -40 | 650 | 700 | 700 | 700
f 4 | 7.3333 | f D | 11.6667 | [8 empty] | -5 | 650 | 700 | 700 | 700
f 5 | 7.3333 | f E | 11.6667 | [8 empty] | 5.5 | 600 | 600 | 700 | 700
f 6 | 8.3333 | f F | 11.6667 | [8 empty] | 15 | 370 | 600 | 600 | 600
f 7 | 9.1667 | [10 empty] | 40 | 370 | 600 | 600 | 600
f 8 | 10
| 30 | 0.5
| [m3/min] | [m3/s]

## Feuil1 (2)
| A1 |  |  | A2
| 1 | 1.04 | 0.8 | 0.61 | 0.74
| 1.02 | 1.12 | 0.96 | 0.92 | 0.85
| 1.1 | 1.11 | 1.01 | 0.64 | 1.1
| 0.98 | 1.06 | 0.82 | 0.62 | 0.94
| A1 | 0.5226 | m² | A2 | 0.1817 | m²
| V1 | 1.0017 | [m/s] | V2 | 0.8025 | [m/s]
| Q1 | 0.52347 | [m3/s] | Q2 | 0.14581 | [m3/s]
Vmoyenne | 0.922 | m/s |  | Tair | 7 | [°C]
Q total | 0.66929 |  |  | Fcomp | 90 | [Hz]

## Feuil1
860 | 600
| 0.516 | m²
0.4128