## AWHPT 6 MR
Setpoint | 1: Ordered | 1: Actual | 1: Remarks | 2: Ordered | 2: Actual | 2: Remarks
254 | 105.6 | 105.6 |  | 105.6 | 105.6
253 | 105.0 | 105.0 |  | 105.0 | 105.0
252 | 104.4 | 104.4 |  | 104.4 | 104.4 |  | Test 1: Starting from 64 and increasing until 254
251 | 103.8 | 103.8 |  | 103.8 | 103.8 |  | Test 2: Step by step, starting from 254 and lowering until 64 steps
250 | 103.2 | 103.2 |  | 103.2 | 103.2
249 | 102.6 | 102.6 |  | 102.6 | 102.6
248 | 102.0 | 102.0 |  | 102.0 | 102.0 |  | Conclusion
247 | 102.0 | 102.0 |  | 102.0 | 102.0
246 | 101.4 | 101.4 |  | 101.4 | 101.4 |  | There are 2 "dead bands" between setpoints 119 & 127 (including) and between 208 & 215 (including). The resulting frequency is determined by the setpoint it was running on before reaching the dead band (upper or lower limit)
245 | 100.8 | 100.8 |  | 100.8 | 100.8 |  | We have determined earlier that it is undesirable to have a frequency lower than 30.0 Hz due to the compressor envelop. This would result in a setpoint bandwidth of 104 (30.0 Hz) to 254 (105.6 Hz).
244 | 100.2 | 100.2 |  | 100.2 | 100.2 |  | Filling in a setpoint lower than 63 results in the outdoor unit turning off, and giving back a setpoint of 0 (on ModBus register 2).
243 | 99.6 | 99.6 |  | 99.6 | 99.6
242 | 99.0 | 99.0 |  | 99.0 | 99.0
241 | 99.0 | 99.0 |  | 99.0 | 99.0
240 | 98.4 | 98.4 |  | 98.4 | 98.4
239 | 97.8 | 97.8 |  | 97.8 | 97.8
238 | 97.2 | 97.2 |  | 97.2 | 97.2
237 | 96.6 | 96.6 |  | 96.6 | 96.6
236 | 96.0 | 96.0 |  | 96.0 | 96.0
235 | 96.0 | 96.0 |  | 96.0 | 96.0
234 | 95.4 | 95.4 |  | 95.4 | 95.4
233 | 94.8 | 94.8 |  | 94.8 | 94.8
232 | 94.2 | 94.2 |  | 94.2 | 94.2
231 | 93.6 | 93.6 |  | 93.6 | 93.6
230 | 93.0 | 93.0 |  | 93.0 | 93.0
229 | 93.0 | 93.0 |  | 93.0 | 93.0
228 | 92.4 | 92.4 |  | 92.4 | 92.4
227 | 91.8 | 91.8 |  | 91.8 | 91.8
226 | 91.2 | 91.2 |  | 91.2 | 91.2
225 | 90.6 | 90.6 |  | 90.6 | 90.6
224 | 90.0 | 90.0 |  | 90.0 | 90.0
223 | 90.0 | 90.0 |  | 90.0 | 90.0
222 | 89.4 | 89.4 |  | 89.4 | 89.4
221 | 88.8 | 88.8 |  | 88.8 | 88.8
220 | 88.2 | 88.2 |  | 88.2 | 88.2
219 | 87.6 | 87.6 |  | 87.6 | 87.6
218 | 87.0 | 87.0 |  | 87.0 | 87.0
217 | 87.0 | 87.0 |  | 87.0 | 87.0
216 | 86.4 | 86.4 |  | 86.4 | 86.4
215 | 85.8 | 81.6 | Ord. ≠ Act. | 85.8 | 86.4 | Ord. ≠ Act.
214 | 85.2 | 81.6 | Ord. ≠ Act. | 85.2 | 86.4 | Ord. ≠ Act.
213 | 84.6 | 81.6 | Ord. ≠ Act. | 84.6 | 86.4 | Ord. ≠ Act.
212 | 84.0 | 81.6 | Ord. ≠ Act. | 84.0 | 86.4 | Ord. ≠ Act.
211 | 84.0 | 81.6 | Ord. ≠ Act. | 84.0 | 86.4 | Ord. ≠ Act.
210 | 83.4 | 81.6 | Ord. ≠ Act. | 83.4 | 86.4 | Ord. ≠ Act.
209 | 82.8 | 81.6 | Ord. ≠ Act. | 82.8 | 86.4 | Ord. ≠ Act.
208 | 82.2 | 81.6 | Ord. ≠ Act. | 82.2 | 86.4 | Ord. ≠ Act.
207 | 81.6 | 81.6 |  | 81.6 | 81.6
206 | 81.0 | 81.0 |  | 81.0 | 81.0
205 | 80.4 | 80.4 |  | 80.4 | 80.4
204 | 80.4 | 80.4 |  | 80.4 | 80.4
203 | 79.8 | 79.8 |  | 79.8 | 79.8
202 | 79.2 | 79.2 |  | 79.2 | 79.2
201 | 78.6 | 78.6 |  | 78.6 | 78.6
200 | 78.0 | 78.0 |  | 78.0 | 78.0
199 | 77.4 | 77.4 |  | 77.4 | 77.4
198 | 77.4 | 77.4 |  | 77.4 | 77.4
197 | 76.8 | 76.8 |  | 76.8 | 76.8
196 | 76.2 | 76.2 |  | 76.2 | 76.2
195 | 75.6 | 75.6 |  | 75.6 | 75.6
194 | 75.0 | 75.0 |  | 75.0 | 75.0
193 | 74.4 | 74.4 |  | 74.4 | 74.4
192 | 74.4 | 74.4 |  | 74.4 | 74.4
191 | 73.8 | 73.8 |  | 73.8 | 73.8
190 | 73.2 | 73.2 |  | 73.2 | 73.2
189 | 72.6 | 72.6 |  | 72.6 | 72.6
188 | 72.0 | 72.0 |  | 72.0 | 72.0
187 | 71.4 | 71.4 |  | 71.4 | 71.4
186 | 71.4 | 71.4 |  | 71.4 | 71.4
185 | 70.8 | 70.8 |  | 70.8 | 70.8
184 | 70.2 | 70.2 |  | 70.2 | 70.2
183 | 69.6 | 69.6 |  | 69.6 | 69.6
182 | 69.0 | 69.0 |  | 69.0 | 69.0
181 | 68.4 | 68.4 |  | 68.4 | 68.4
180 | 68.4 | 68.4 |  | 68.4 | 68.4
179 | 67.8 | 67.8 |  | 67.8 | 67.8
178 | 67.2 | 67.2 |  | 67.2 | 67.2
177 | 66.6 | 66.6 |  | 66.6 | 66.6
176 | 66.0 | 66.0 |  | 66.0 | 66.0
175 | 65.4 | 65.4 |  | 65.4 | 65.4
174 | 65.4 | 65.4 |  | 65.4 | 65.4
173 | 64.8 | 64.8 |  | 64.8 | 64.8
172 | 64.2 | 64.2 |  | 64.2 | 64.2
171 | 63.6 | 63.6 |  | 63.6 | 63.6
170 | 63.0 | 63.0 |  | 63.0 | 63.0
169 | 62.4 | 62.4 |  | 62.4 | 62.4
168 | 62.4 | 62.4 |  | 62.4 | 62.4
167 | 61.8 | 61.8 |  | 61.8 | 61.8
166 | 61.2 | 61.2 |  | 61.2 | 61.2
165 | 60.6 | 60.6 |  | 60.6 | 60.6
164 | 60.0 | 60.0 |  | 60.0 | 60.0
163 | 59.4 | 59.4 |  | 59.4 | 59.4
162 | 59.4 | 59.4 |  | 59.4 | 59.4
161 | 58.8 | 58.8 |  | 58.8 | 58.8
160 | 58.2 | 58.2 |  | 58.2 | 58.2
159 | 57.6 | 57.6 |  | 57.6 | 57.6
158 | 57.0 | 57.0 |  | 57.0 | 57.0
157 | 56.4 | 56.4 |  | 56.4 | 56.4
156 | 55.8 | 55.8 |  | 55.8 | 55.8
155 | 55.8 | 55.8 |  | 55.8 | 55.8
154 | 55.2 | 55.2 |  | 55.2 | 55.2
153 | 54.6 | 54.6 |  | 54.6 | 54.6
152 | 54.0 | 54.0 |  | 54.0 | 54.0
151 | 53.4 | 53.4 |  | 53.4 | 53.4
150 | 52.8 | 52.8 |  | 52.8 | 52.8
149 | 52.8 | 52.8 |  | 52.8 | 52.8
148 | 52.2 | 52.2 |  | 52.2 | 52.2
147 | 51.6 | 51.6 |  | 51.6 | 51.6
146 | 51.0 | 51.0 |  | 51.0 | 51.0
145 | 50.4 | 50.4 |  | 50.4 | 50.4
144 | 49.8 | 49.8 |  | 49.8 | 49.8
143 | 49.8 | 49.8 |  | 49.8 | 49.8
142 | 49.2 | 49.2 |  | 49.2 | 49.2
141 | 48.6 | 48.6 |  | 48.6 | 48.6
140 | 48.0 | 48.0 |  | 48.0 | 48.0
139 | 47.4 | 47.4 |  | 47.4 | 47.4
138 | 46.8 | 46.8 |  | 46.8 | 46.8
137 | 46.8 | 46.8 |  | 46.8 | 46.8
136 | 46.2 | 46.2 |  | 46.2 | 46.2
135 | 45.6 | 45.6 |  | 45.6 | 45.6
134 | 45.0 | 45.0 |  | 45.0 | 45.0
133 | 44.4 | 44.4 |  | 44.4 | 44.4
132 | 43.8 | 43.8 |  | 43.8 | 43.8
131 | 43.8 | 43.8 |  | 43.8 | 43.8
130 | 43.2 | 43.2 |  | 43.2 | 43.2
129 | 42.6 | 42.6 |  | 42.6 | 42.6
128 | 42.0 | 42.0 |  | 42.0 | 42.0
127 | 41.4 | 37.2 | Ord. ≠ Act. | 41.4 | 42.0 | Ord. ≠ Act.
126 | 40.8 | 37.2 | Ord. ≠ Act. | 40.8 | 42.0 | Ord. ≠ Act.
125 | 40.8 | 37.2 | Ord. ≠ Act. | 40.8 | 42.0 | Ord. ≠ Act.
124 | 40.2 | 37.2 | Ord. ≠ Act. | 40.2 | 42.0 | Ord. ≠ Act.
123 | 39.6 | 37.2 | Ord. ≠ Act. | 39.6 | 42.0 | Ord. ≠ Act.
122 | 39.0 | 37.2 | Ord. ≠ Act. | 39.0 | 42.0 | Ord. ≠ Act.
121 | 38.4 | 37.2 | Ord. ≠ Act. | 38.4 | 42.0 | Ord. ≠ Act.
120 | 37.8 | 37.2 | Ord. ≠ Act. | 37.8 | 42.0 | Ord. ≠ Act.
119 | 37.8 | 37.2 | Ord. ≠ Act. | 37.8 | 42.0 | Ord. ≠ Act.
118 | 37.2 | 37.2 |  | 37.2 | 37.2
117 | 36.6 | 36.6 |  | 36.6 | 36.6
116 | 36.0 | 36.0 |  | 36.0 | 36.0
115 | 35.4 | 35.4 |  | 35.4 | 35.4
114 | 34.8 | 34.8 |  | 34.8 | 34.8
113 | 34.8 | 34.8 |  | 34.8 | 34.8
112 | 34.2 | 34.2 |  | 34.2 | 34.2
111 | 33.6 | 33.6 |  | 33.6 | 33.6
110 | 33.0 | 33.0 |  | 33.0 | 33.0
109 | 32.4 | 32.4 |  | 32.4 | 32.4
108 | 31.8 | 31.8 |  | 31.8 | 31.8
107 | 31.2 | 31.2 |  | 31.2 | 31.2
106 | 31.2 | 31.2 |  | 31.2 | 31.2
105 | 30.6 | 30.6 |  | 30.6 | 30.6
104 | 30.0 | 30.0 |  | 30.0 | 30.0
103 | 29.4 | 29.4 |  | 29.4 | 29.4
102 | 28.8 | 28.8 |  | 28.8 | 28.8
101 | 28.2 | 28.2 |  | 28.2 | 28.2
100 | 28.2 | 28.2 |  | 28.2 | 28.2
99 | 27.6 | 27.6 |  | 27.6 | 27.6
98 | 27.0 | 27.0 |  | 27.0 | 27.0
97 | 26.4 | 26.4 |  | 26.4 | 26.4
96 | 25.8 | 25.8 |  | 25.8 | 25.8
95 | 25.2 | 25.2 |  | 25.2 | 25.2
94 | 25.2 | 25.2 |  | 25.2 | 25.2
93 | 24.6 | 24.6 |  | 24.6 | 24.6
92 | 24.0 | 24.0 |  | 24.0 | 24.0
91 | 23.4 | 23.4 |  | 23.4 | 23.4
90 | 22.8 | 22.8 |  | 22.8 | 22.8
89 | 22.2 | 22.2 |  | 22.2 | 22.2
88 | 22.2 | 22.2 |  | 22.2 | 22.2
87 | 21.6 | 21.6 |  | 21.6 | 21.6
86 | 21.0 | 21.0 |  | 21.0 | 21.0
85 | 20.4 | 20.4 |  | 20.4 | 20.4
84 | 19.8 | 19.8 |  | 19.8 | 19.8
83 | 19.2 | 19.2 |  | 19.2 | 19.2
82 | 19.2 | 19.2 |  | 19.2 | 19.2
81 | 18.6 | 18.6 |  | 18.6 | 18.6
80 | 18.0 | 18.0 |  | 18.0 | 18.0
79 | 17.4 | 17.4 |  | 17.4 | 17.4
78 | 16.8 | 16.8 |  | 16.8 | 16.8
77 | 16.2 | 16.2 |  | 16.2 | 16.2
76 | 16.2 | 16.2 |  | 16.2 | 16.2
75 | 15.6 | 15.6 |  | 15.6 | 15.6
74 | 15.0 | 15.0 |  | 15.0 | 15.0
73 | 14.4 | 14.4 |  | 14.4 | 14.4
72 | 13.8 | 13.8 |  | 13.8 | 13.8
71 | 13.2 | 13.2 |  | 13.2 | 13.2
70 | 13.2 | 13.2 |  | 13.2 | 13.2
69 | 12.6 | 12.6 |  | 12.6 | 12.6
68 | 12.0 | 12.0 |  | 12.0 | 12.0
67 | 11.4 | 11.4 |  | 11.4 | 11.4
66 | 10.8 | 10.8 |  | 10.8 | 10.8
65 | 10.2 | 10.2 |  | 10.2 | 10.2
64 | 10.2 | 10.2 |  | 10.2 | 10.2

## AWHPT 4 MR
1: Ordered | 1: Actual | 1: Remarks | 2: Ordered | 2: Actual | 2: Remarks
Test 1: Starting from 64 and increasing until 254
Test 2: Step by step, starting from 254 and lowering until 64 steps
Conclusion
There is a "dead band" between setpoints 76 & 97 (including). The resulting frequency is determined by the setpoint it was running on before reaching the dead band. If it was 98 or higher, the frequency in the dead band is 28.8, if it was 75 or lower, the frequency will be 19.2.
We have determined earlier that it is undesirable to have a frequency lower than 30.0 Hz due to the compressor envelop. This would result in a setpoint bandwidth of 101 (30.0 Hz) to 254 (93.6 Hz).
Filling in a setpoint lower than 63 results in the outdoor unit turning off, and giving back a setpoint of 0 (on ModBus register 2).